## PEB Specifications
Sr.No. |  |  | Sr no. | Parameter | Details
1 | Date | 2025-09-02 | 1 | Desing code | AISC code
2 | Structure application | Fabrication Shed | 1 | Dead Load in kN/m2 | 0.1
3 | Proposal Id | C529-013 | 2 | Live Load in kN/m2 | 0.57
|  |  | 3 | Collateral load kN/m2 | 0
4 | Building No. | 1 | 4 | Max wind speed in m/s | 39
5 | Option | 1 | 5 | Max rainfall intensity in mm/hr | 150
6 | Revision | 0 | 6 | Exposure category | B
7 | Area (sqm) | 960.6345 | 7 | Seismic zone co-efficient (III) | 0.16
8 | Design Software | MBS | 8 | Maximum temperate variation | 20
Sr.No. | Parameter | Details | Sr no. | Parameter | Details
1 | Building type | Clear Span | 1 | Frames Vertical deflection | Span/150
2 | Length in m (o/o of steel) | 28.65 | 2 | Frames Horizontal deflection | Height/100
3 | Width in m (o/o of steel) | 33.53 | 3 | Purlins | Span/150
4 | Left eave height in m | 9 | 4 | Girts | Span/120
5 | Right eave height in m | 9 | 5 | Crane beams | Span/600
6 | Ridge line distance | 16.765 | 6 | Mezzanine beams | Span/240
7 | Roof slope (?:100) | 10/100 | 7 | Misc
8 | Left end wall bay spacing in m | 5@6.706 | Sr no. | Assumption/Remark | Details
9 | Right end wall bay spacing in m | 5@6.706 | 1 | Hot rolled sections grade (Mpa) | 250
10 | Side wall bay spacing | 1@7.16+2@7.165+1@7.16 | 2 | Cold form sections grade (Mpa) | 350
11 | Wall bracing type | Rod | 3 | Primary sections grade (Mpa) | 350
12 | Roof bracing type | Rod | 4 | Building design condition | Enclosed
13 | Roof sheeting | 0.45mm aluzinc | 4 | Minimum web thickness in mm | 4
14 | Wall sheeting | 0.45mm aluzinc | 5 | Minimum flange thickness in mm | 5
15 | Doors | 4.5x4.5 | 6 | Minimum flange width in mm | 125
16 | Windows (4nos.) | 2x1.5 | 7 | Minimum web depth in mm | 250
17 | Block wall in m | 3 | 8 | Minimum cold form thickness in mm | 1.5
18 | Rigid frames interior column locations |  | 9 | Sheeting profile width & length in m | 1.22 & 7.65
Sr no. | Item | Details | 10 | Connection bolts grade | High strength bolts (ASTM A325 or equivalent)
1 | Canopy Extension in m | 3
2 | Slope | 10/100
3 | Clear top height in m | 3.5
Sr no. | Accessories
1 | Braced bays (Bay id) | 1 4
2 | Skylights (FRP 3.25m x 1m) | 8
3 | Turbo Ventilators (600 mm throat diameter) | 8
4 | Base Elevation
5 | Bay Id @ Left end wall | NA
6 | Bay Id @ Front side wall | NA
7 | Bay Id @ Right end wall | NA
8 | Bay Id @ Back side wall | NA

## Crane & mezzanine
Sr no. | Parameter | Details
1 | Crane Capacity in kN
2 | Crane beam top height in m
3 | Crane span in m
4 | Crane running length in m
5 | Crane class | II (Normal duty)
6 | Crane Type | Top running
7 | Type of Girder | Single
8 | Bridge Weight in MT
9 | Hoist/Trolley Weight in MT
10 | Number of Wheels
11 | Wheel Load in MT
12 | Wheel Base in mm
MEZZANINE
Sr no. | Parameter | Details
1 | Location
2 | Loading
MEZZANINE Live load in kN/m2
MEZZANINE Dead load in kN/m2
MEZZANINE Collateral load in kN/m2
3 | Dimensions | -
Length in m
Width in m
Top of the Mezzanine Floor in m
Depth of mezzanine slab in mm
Deck sheeting thickness
4 | Accessories
| Staircase Nos. | 1
| Type | Double staircase with intermediate landing
| Handrail (1m height ) | on the open side of mezzanine
Wall Lights (FRP 3.25m x 1m)
Skylights (FRP 3.25m x 1m)
Turbo Ventilators(600mm TD)

## Extras
Sr no. | Items | Details
1 | Cable tray brackets | bracket lenth
4 | Walkway details | Length in m: Width in m: Height in m: Loading:
7 | Jack beam | location
8 | Parttion wall | Length in m: Width in m: Height in m: Location:
11 | Roof Insulation
12 | Wall Insulation
13 | Monkey laader | location
14 | Fascia | Length in m: Width in m: Height in m:
16 | Gable extension in m
17 | Eave extension in m
18 | Roof Monitor | Length in m: Width in m: Height in m:
19 | Cage ladder | NA
20 | Ridge Ventilators | NA
21 | Any other | NA

## Notes
Sr no. | Parameter | Value
1 | Automatic 1st girt location | 80mm above block wall height
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28